- Cable marking and labeling shall use the designations indicated on the Cable Schedule.  Additional information (i.e. MBRM, Motion, etc.) is at the discretion of the installer.

- Installer shall mark each end of the cable with specified label designations.  Marking or label method is at installers discretion but must be accomplished in a permanent and clearly readable manner.

- Maintain at least 12" separation from all electrical alternating current (A.C.) wiring where possible.  When not possible cross electrical wiring at 90 degrees.  Increase separation to at least 24” for high current circuits such as ranges, cooling compressors, etc, and pay particular attention to avoiding cable runs in close proximity to dimmers, fluorescent fixtures and ballasts, and  low voltage transformers.

- Recommended practice for installing coax includes:

Do not splice or make sharp bends in cable

Do not staple or attach coax in a way that can deform the cable

Do not coil cable tightly and push back into gang boxes

Do not use crimp type connectors.  Use a compression fitting connector such as LRC Snap n Seal Type 6QS or Raychem EZF-6

Seal or cap all coax end to prevent moisture intrusion during period between rough-in and trim phases.

- Provide excess trim lengths of  36" at main panel wiring locations and at least 24" at other locations.  All wiring should be bagged or sealed to prevent moisture intrusion and protect against drywall mud and paint prior to trim phase.

- Locate wall outlets aligned with electrical outlets.

- Locate touch panel 57” Above Finished Floor (A.F.F.).

- Bag or dip in sealer all wire ends after pre-wire.

- Splicing is not acceptable.

- Take extra care when running category 5 cable for data/LAN runs.  Failure to follow these suggestion can result in poor performance.

Do not splice or make sharp bends in cable

Do not staple or attach cable in a way that can deform the cable

Do not pull cable with excessive force that can stretch or deform cable

# Text boxes

Low Voltage Pre-Wire Installation Guidelines

<<Company Name>>

<<Address>>

<<City  State  ZIP>>

<<Telephone>>

<<Website>>